## Superheated Rankine Cycle
Analysis of a Superheated Rankine Cycle
|  | Thermodynamic model: | IF97
Design Data
State 1: | liquid at 303.15 K |  |  |  | 303.15 | K | = | 30 | °C
State 2: | 8 MPa |  |  |  | 8 | MPa | = | 80 | bar
State 3: | superheated steam at 673.15 K |  |  |  | 673.15 | K | = | 400 | °C
State 4: | 303.15 K |  |  |  | 303.15 | K | = | 30 | °C
Isentropic efficiencies
Feedwater pump: |  | ηis = | 0.65
Turbine: |  | ηis = | 0.85
Pump (state 1 & 2)
h1 = | 125.7452 | kJ/kg | [8 empty] | s [kJ/kg] | T [°C]
s1 = | 0.43679 | kJ/kgK | [7 empty] | 1 | 0.43679 | 30
P1 = | 0.042467 | bar |  | Approximation (calculation with vDP) | [5 empty] | 2 | 0.451 | 31.2168
|  |  |  | v1 = | 0.0010044 | m3/kg |  |  |  | 2a | 3.2077 | 295.0091
h2,is = | 133.7622 | kJ/kg |  | h2,is = | 133.7762 | kJ/kg |  |  |  | 2b | 5.7448 | 295.0091
h2 = | 138.079 | kJ/kg | [7 empty] | 3 | 6.3657 | 400
[10 empty] | 4 | 6.9675 | 30
wpump = | 12.3339 | kJ/kg | [7 empty] | 1 | 0.43679 | 30
Boiler (state 3)
h3 = | 3139.3106 | kJ/kg
qboiler = | 3001.2316 | kJ/kg
Turbine (state 4)
P3 = P2 = | 80 | bar
s3 = | 6.3657 | kJ/kgK
h4,is = | 1923.0881 | kJ/kg
h4 = | 2105.5215 | kJ/kg
q4 = | 0.81478
wturb = | 1033.7892 | kJ/kg
System efficiency
η = | 0.34035

## data T-s chart
IF97
Product_Name | Scientific_Name | Chemical_Formula | FluidPop Name | Tc [°C] | Pc [bar] | vc [m3/kg] | MW [kg/mol] | Tmin [°C] | Tmax [°C]
Water | Water | H2O | Water | 373.946 | 220.64 | 0.0031056 | 0.018015 | 0.01 | 800
[28 empty] | Pmax [bar]= | 661.92 | Pmin [bar]= | 0.0061211
q=0 |  |  | q=1 | [18 empty] | q= | 0.25 | q= | 0.5 | q= | 0.75
DT [°C]= | 3.7394 |  | DT [°C]= | 3.7394 |  | P [bar]= | 1 | P [bar]= | 50 | P [bar]= | 220.64 | P [bar]= | 661.92 | v[m3/kg]= | 0.5 | v[m3/kg]= | 0.01 | v[m3/kg]= | 0.0031056 | v[m3/kg]= | 0.002 | DT [°C]= | 3.7394 | DT [°C]= | 3.7394 | DT [°C]= | 3.7394 | h[kJ/kg]= | 1000 |  |  | h[kJ/kg]= | 2600 |  | h[kJ/kg]= | 3000 |  | h[kJ/kg]= | 3600
s [kJ/kg] | T [°C] |  | s [kJ/kg] | T [°C] |  | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | s [kJ/kg] | T [°C] | P[bar] | s [kJ/kg] | T [°C] |  | P[bar] | s [kJ/kg] | T [°C] | P[bar] | s [kJ/kg] | T [°C] | P[bar] | s [kJ/kg] | T [°C]
0.00077227 | 0.06 |  | 9.1542 | 0.06 |  | 6.6684e-06 | 0.01 | 0.00029189 | 0.01 | 0.00060978 | 0.01 | -0.0027094 | 0.01 | 0.022178 | 0.01 | 0.00039993 | 0.01 | 9.3512e-05 | 0.01 | 4.4374e-05 | 0.01 | 2.2889 | 0.01 | 4.5777 | 0.01 | 6.8666 | 0.01 | 661.92 | 2.4818 | 227.1897 |  | 661.92 | 4.9506 | 513.9923 | 661.92 | 5.4394 | 579.8707 | 661.92 | 6.0927 | 724.2775
0.058053 | 3.7994 |  | 9.0557 | 3.7994 |  | 0.15063 | 9.9696 | 0.38553 | 26.4033 | 0.11189 | 7.4887 | 0.11246 | 8.0099 | 0.15796 | 8.0099 | 0.12214 | 8.0099 | 0.12163 | 8.0099 | 0.12155 | 8.0099 | 2.3072 | 3.7494 | 4.5572 | 3.7494 | 6.8071 | 3.7494 | 535.3463 | 2.5107 | 228.4956 |  | 549.536 | 4.9942 | 494.6408 | 634.34 | 5.4525 | 574.6797 | 634.34 | 6.1094 | 719.7989
0.11444 | 7.5387 |  | 8.9607 | 7.5387 |  | 0.29547 | 19.9292 | 0.73741 | 52.7966 | 0.22024 | 14.9674 | 0.22496 | 16.0098 | 0.29715 | 16.0098 | 0.24017 | 16.0098 | 0.23937 | 16.0098 | 0.23924 | 16.0098 | 2.3257 | 7.4887 | 4.5378 | 7.4887 | 6.7499 | 7.4887 | 408.7725 | 2.5399 | 229.6666 |  | 437.152 | 5.0461 | 468.9843 | 606.76 | 5.4661 | 569.2136 | 606.76 | 6.1267 | 715.1586
0.16998 | 11.2781 |  | 8.8688 | 11.2781 |  | 0.43523 | 29.8888 | 1.0625 | 79.1899 | 0.32586 | 22.4462 | 0.33477 | 24.0097 | 0.44288 | 24.0097 | 0.35496 | 24.0097 | 0.35372 | 24.0097 | 0.35352 | 24.0097 | 2.3444 | 11.2281 | 4.5196 | 11.2281 | 6.6948 | 11.2281 | 282.1988 | 2.5693 | 230.6783 |  | 324.768 | 5.1125 | 433.5964 | 579.18 | 5.4804 | 563.4522 | 579.18 | 6.145 | 710.3489
0.22472 | 15.0174 |  | 8.78 | 15.0174 |  | 0.57037 | 39.8484 | 1.3657 | 105.5831 | 0.4289 | 29.9249 | 0.44194 | 32.0096 | 0.59877 | 32.0096 | 0.46683 | 32.0096 | 0.46498 | 32.0096 | 0.46468 | 32.0096 | 2.3633 | 14.9674 | 4.5026 | 14.9674 | 6.6419 | 14.9674 | 155.625 | 2.5991 | 231.4984 |  | 212.384 | 5.2093 | 381.9924 | 551.6 | 5.4954 | 557.3729 | 551.6 | 6.1641 | 705.3618
0.27872 | 18.7568 |  | 8.6941 | 18.7568 |  | 0.70127 | 49.808 | 1.6509 | 131.9764 | 0.52947 | 37.4036 | 0.54655 | 40.0095 | 0.76909 | 40.0095 | 0.5761 | 40.0095 | 0.57338 | 40.0095 | 0.57295 | 40.0095 | 2.3823 | 18.7068 | 4.4866 | 18.7068 | 6.5909 | 18.7068 | 29.0513 | 2.6293 | 232.0829 |  | 100 | 5.4011 | 310.9995 | 524.02 | 5.5111 | 550.9505 | 524.02 | 6.1843 | 700.1891
0.33198 | 22.4962 |  | 8.6109 | 22.4962 |  | 0.82825 | 59.7676 | 1.9213 | 158.3697 | 0.62772 | 44.8823 | 0.64868 | 48.0094 | 0.95877 | 48.0094 | 0.68303 | 48.0094 | 0.67915 | 48.0094 | 0.67853 | 48.0094 | 2.4015 | 22.4462 | 4.4717 | 22.4462 | 6.5418 | 22.4462 | 27.6237 | 2.6297 | 229.3252 |  | 80 | 5.4657 | 295.0091 | 496.44 | 5.5277 | 544.1572 | 496.44 | 6.2056 | 694.8221
0.38455 | 26.2355 |  | 8.5305 | 26.2355 |  | 0.95162 | 69.7271 | 2.1801 | 184.763 | 0.72374 | 52.361 | 0.74843 | 56.0093 | 1.1734 | 56.0093 | 0.78789 | 56.0093 | 0.78246 | 56.0093 | 0.78159 | 56.0093 | 2.4208 | 26.1855 | 4.4577 | 26.1855 | 6.4946 | 26.1855 | 26.1961 | 2.6303 | 226.4554 |  | 70 | 5.5059 | 285.83 | 468.86 | 5.5452 | 536.9614 | 468.86 | 6.2282 | 689.2516
0.43645 | 29.9749 |  | 8.4526 | 29.9749 |  | 1.0716 | 79.6867 | 2.4303 | 211.1563 | 0.81766 | 59.8398 | 0.84592 | 64.0092 | 1.4194 | 64.0092 | 0.89095 | 64.0092 | 0.88351 | 64.0092 | 0.88232 | 64.0092 | 2.4402 | 29.9249 | 4.4447 | 29.9249 | 6.4492 | 29.9249 | 24.7686 | 2.631 | 223.4624 |  | 60 | 5.5537 | 275.5864 | 441.28 | 5.5638 | 529.3277 | 441.28 | 6.2523 | 683.4681
0.48769 | 33.7142 |  | 8.3772 | 33.7142 |  | 1.1885 | 89.6463 | 2.6756 | 237.5496 | 0.90959 | 67.3185 | 0.94126 | 72.0091 | 1.7037 | 72.0091 | 0.99247 | 72.0091 | 0.98247 | 72.0091 | 0.98086 | 72.0091 | 2.4598 | 33.6642 | 4.4326 | 33.6642 | 6.4054 | 33.6642 | 23.341 | 2.632 | 220.3331 |  | 50 | 5.6121 | 263.9429 | 413.7 | 5.5837 | 521.2159 | 413.7 | 6.278 | 677.4615
0.53831 | 37.4536 |  | 8.3041 | 37.4536 |  | 1.3026 | 99.6059 | 2.9207 | 263.9429 | 0.99962 | 74.7972 | 1.0345 | 80.009 | 2.0337 | 80.009 | 1.0927 | 80.009 | 1.0795 | 80.009 | 1.0774 | 80.009 | 2.4795 | 37.4036 | 4.4214 | 37.4036 | 6.3632 | 37.4036 | 21.9134 | 2.6332 | 217.0522 |  | 20 | 5.9306 | 212.3845 | 386.12 | 5.6051 | 512.58 | 386.12 | 6.3057 | 671.2213
0.58832 | 41.193 |  | 8.2333 | 41.193 |  | 1.9082 | 99.6059 | 3.226 | 263.9429 | 1.0879 | 82.2759 | 1.1259 | 88.0089 | 2.4177 | 88.0089 | 1.192 | 88.0089 | 1.1747 | 88.0089 | 1.172 | 88.0089 | 2.4993 | 41.143 | 4.411 | 41.143 | 6.3226 | 41.143 | 20.4859 | 2.6347 | 213.6015 |  | 10 | 6.194 | 179.8856 | 358.54 | 5.6281 | 503.367 | 358.54 | 6.3355 | 664.7362
0.63774 | 44.9323 |  | 8.1647 | 44.9323 |  | 2.5138 | 99.6059 | 3.5313 | 263.9429 | 1.1744 | 89.7546 | 1.2153 | 96.0088 | 2.8641 | 96.0088 | 1.2905 | 96.0088 | 1.2683 | 96.0088 | 1.2648 | 96.0088 | 2.5192 | 44.8823 | 4.4013 | 44.8823 | 6.2834 | 44.8823 | 19.0583 | 2.6365 | 209.9591 |  | 2 | 6.8568 | 120.2115 | 330.96 | 5.6533 | 493.5154 | 330.96 | 6.3679 | 657.9945
0.68658 | 48.6717 |  | 8.0981 | 48.6717 |  | 3.1194 | 99.6059 | 3.8366 | 263.9429 | 1.2593 | 97.2334 | 1.303 | 104.0087 | 3.3817 | 104.0087 | 1.3885 | 104.0087 | 1.3605 | 104.0087 | 1.356 | 104.0087 | 2.5392 | 48.6217 | 4.3924 | 48.6217 | 6.2457 | 48.6217 | 17.6308 | 2.6387 | 206.0983 |  | 0.15714 | 7.9909 | 54.9374 | 303.38 | 5.6809 | 482.9529 | 303.38 | 6.4034 | 650.9836
0.73486 | 52.411 |  | 8.0335 | 52.411 |  | 3.7251 | 99.6059 | 4.1419 | 263.9429 | 1.3427 | 104.7121 | 1.389 | 112.0086 | 3.9799 | 112.0086 | 1.4863 | 112.0086 | 1.4512 | 112.0086 | 1.4456 | 112.0086 | 2.5593 | 52.361 | 4.3843 | 52.361 | 6.2093 | 52.361 | 16.2032 | 2.6413 | 201.9863 |  | 0.14959 | 8.0135 | 54.8323 | 275.8 | 5.7115 | 471.5934 | 275.8 | 6.4425 | 643.69
0.78261 | 56.1504 |  | 7.9708 | 56.1504 |  | 4.3307 | 99.6059 | 4.4472 | 263.9429 | 1.4246 | 112.1908 | 1.4733 | 120.0085 | 4.6678 | 120.0085 | 1.5842 | 120.0085 | 1.5408 | 120.0085 | 1.5338 | 120.0085 | 2.5794 | 56.1004 | 4.3768 | 56.1004 | 6.1742 | 56.1004 | 14.7756 | 2.6446 | 197.5816 |  | 0.14204 | 8.0374 | 54.7315 | 248.22 | 5.7459 | 459.3328 | 248.22 | 6.4861 | 636.0994
0.82983 | 59.8898 |  | 7.9099 | 59.8898 |  | 4.9363 | 99.6059 | 4.7525 | 263.9429 | 1.5051 | 119.6695 | 1.5562 | 128.0084 | 5.4552 | 128.0084 | 1.6823 | 128.0084 | 1.6292 | 128.0084 | 1.6207 | 128.0084 | 2.5996 | 59.8398 | 4.37 | 59.8398 | 6.1404 | 59.8398 | 13.3481 | 2.6486 | 192.831 |  | 0.13449 | 8.0625 | 54.6309 | 220.64 | 5.785 | 446.0435 | 220.64 | 6.5352 | 628.1963
0.87654 | 63.6291 |  | 7.8508 | 63.6291 |  | 5.5419 | 99.6059 | 5.0578 | 263.9429 | 1.5843 | 127.1482 | 1.6376 | 136.0083 | 6.3513 | 136.0083 | 1.781 | 136.0083 | 1.7167 | 136.0083 | 1.7064 | 136.0083 | 2.6198 | 63.5791 | 4.3638 | 63.5791 | 6.1077 | 63.5791 | 11.9205 | 2.6536 | 187.6645 |  | 0.12694 | 8.0891 | 54.5302 | 193.06 | 5.8301 | 431.5378 | 193.06 | 6.5913 | 619.9639
0.92276 | 67.3685 |  | 7.7934 | 67.3685 |  | 6.1476 | 99.6059 | 5.3631 | 263.9429 | 1.6622 | 134.627 | 1.7175 | 144.0082 | 6.937 | 144.0082 | 1.8805 | 144.0082 | 1.8033 | 144.0082 | 1.7909 | 144.0082 | 2.6402 | 67.3185 | 4.3582 | 67.3185 | 6.0762 | 67.3185 | 10.4929 | 2.6598 | 181.9873 |  | 0.11939 | 8.1173 | 54.4297 | 165.48 | 5.8833 | 415.6281 | 165.48 | 6.6568 | 611.3844
0.96849 | 71.1078 |  | 7.7376 | 71.1078 |  | 6.7532 | 99.6059 | 5.6684 | 263.9429 | 1.739 | 142.1057 | 1.7962 | 152.0081 | 6.9686 | 152.0081 | 1.981 | 152.0081 | 1.8892 | 152.0081 | 1.8744 | 152.0081 | 2.6605 | 71.0578 | 4.3531 | 71.0578 | 6.0457 | 71.0578 | 9.0654 | 2.6676 | 175.6657 |  | 0.11184 | 8.1473 | 54.3292 | 137.9 | 5.9478 | 398.0254 | 137.9 | 6.735 | 602.438
1.0138 | 74.8472 |  | 7.6834 | 74.8472 |  | 7.3588 | 99.6059 | 5.9737 | 263.9429 | 1.8146 | 149.5844 | 1.8736 | 160.008 | 6.9991 | 160.008 | 2.0828 | 160.008 | 1.9744 | 160.008 | 1.957 | 160.008 | 2.6809 | 74.7972 | 4.3486 | 74.7972 | 6.0163 | 74.7972 | 7.6378 | 2.6778 | 168.5017 |  | 0.10428 | 8.1795 | 54.2287 | 110.32 | 6.0293 | 378.3448 | 110.32 | 6.8318 | 593.1037
1.0586 | 78.5866 |  | 7.6306 | 78.5866 |  | 7.4066 | 108.3608 | 6.0259 | 270.6436 | 1.8892 | 157.0631 | 1.9498 | 168.0079 | 7.0288 | 168.0079 | 2.186 | 168.0079 | 2.059 | 168.0079 | 2.0387 | 168.0079 | 2.7013 | 78.5366 | 4.3446 | 78.5366 | 5.988 | 78.5366 | 6.2103 | 2.6914 | 160.1832 |  | 0.096734 | 8.2141 | 54.1283 | 105.9074 | 6.0444 | 374.9689 | 105.9074 | 6.8496 | 591.5728
1.1029 | 82.3259 |  | 7.5792 | 82.3259 |  | 7.4527 | 117.1158 | 6.0732 | 277.3443 | 1.9628 | 164.5418 | 2.0248 | 176.0078 | 7.0576 | 176.0078 | 2.291 | 176.0078 | 2.1433 | 176.0078 | 2.1196 | 176.0078 | 2.7217 | 82.2759 | 4.3411 | 82.2759 | 5.9605 | 82.2759 | 4.7827 | 2.7107 | 150.1695 |  | 0.089183 | 8.2515 | 54.028 | 101.4949 | 6.0604 | 371.5229 | 101.4949 | 6.8682 | 590.0312
1.1469 | 86.0653 |  | 7.5293 | 86.0653 |  | 7.4975 | 125.8707 | 6.1169 | 284.045 | 2.0355 | 172.0206 | 2.0988 | 184.0077 | 7.0858 | 184.0077 | 2.398 | 184.0077 | 2.2271 | 184.0077 | 2.1998 | 184.0077 | 2.7422 | 86.0153 | 4.3381 | 86.0153 | 5.934 | 86.0153 | 3.3551 | 2.7401 | 137.3818 |  | 0.081632 | 8.2922 | 53.9277 | 97.0823 | 6.0771 | 368.0036 | 97.0823 | 6.8877 | 588.479
1.1904 | 89.8046 |  | 7.4806 | 89.8046 |  | 7.541 | 134.6256 | 6.1579 | 290.7457 | 2.1072 | 179.4993 | 2.1717 | 192.0076 | 7.1133 | 192.0076 | 2.507 | 192.0076 | 2.3108 | 192.0076 | 2.2793 | 192.0076 | 2.7627 | 89.7546 | 4.3355 | 89.7546 | 5.9084 | 89.7546 | 1.9276 | 2.7931 | 119.0492 |  | 0.07408 | 8.3369 | 53.8275 | 92.6698 | 6.0947 | 364.4076 | 92.6698 | 6.9082 | 586.9159
1.2335 | 93.544 |  | 7.4332 | 93.544 |  | 7.5833 | 143.3805 | 6.1967 | 297.4464 | 2.1782 | 186.978 | 2.2437 | 200.0075 | 7.1402 | 200.0075 | 2.6185 | 200.0075 | 2.3943 | 200.0075 | 2.3583 | 200.0075 | 2.7831 | 93.494 | 4.3334 | 93.494 | 5.8836 | 93.494 | 0.5 | 2.9516 | 81.3167 |  | 0.066529 | 8.3864 | 53.7273 | 88.2572 | 6.1133 | 360.7313 | 88.2572 | 6.9296 | 585.3419
1.2762 | 97.2834 |  | 7.3869 | 97.2834 |  | 7.6247 | 152.1355 | 6.2336 | 304.1472 | 2.2484 | 194.4567 | 2.3148 | 208.0074 | 7.1666 | 208.0074 | 2.7325 | 208.0074 | 2.4777 | 208.0074 | 2.4368 | 208.0074 | 2.8036 | 97.2334 | 4.3316 | 97.2334 | 5.8596 | 97.2334 | 0.47531 | 2.9583 | 80.0603 |  | 0.058978 | 8.4419 | 53.6272 | 83.8447 | 6.133 | 356.9706 | 83.8447 | 6.9523 | 583.7569
1.3186 | 101.0227 |  | 7.3419 | 101.0227 |  | 7.6651 | 160.8904 | 6.2688 | 310.8479 | 2.318 | 201.9354 | 2.385 | 216.0073 | 7.1925 | 216.0073 | 2.8492 | 216.0073 | 2.5611 | 216.0073 | 2.5149 | 216.0073 | 2.8241 | 100.9727 | 4.3302 | 100.9727 | 5.8363 | 100.9727 | 0.45061 | 2.9653 | 78.7478 |  | 0.051427 | 8.505 | 53.5271 | 79.4321 | 6.1538 | 353.1213 | 79.4321 | 6.9762 | 582.1608
1.3605 | 104.7621 |  | 7.2979 | 104.7621 |  | 7.7046 | 169.6453 | 6.3027 | 317.5486 | 2.3869 | 209.4142 | 2.4544 | 224.0072 | 7.2179 | 224.0072 | 2.9689 | 224.0072 | 2.6446 | 224.0072 | 2.5926 | 224.0072 | 2.8446 | 104.7121 | 4.3292 | 104.7121 | 5.8138 | 104.7121 | 0.42592 | 2.9728 | 77.3734 |  | 0.043876 | 8.5782 | 53.427 | 75.0196 | 6.176 | 349.1788 | 75.0196 | 7.0015 | 580.5534
1.4021 | 108.5014 |  | 7.255 | 108.5014 |  | 7.7433 | 178.4003 | 6.3354 | 324.2493 | 2.4552 | 216.8929 | 2.5231 | 232.0071 | 7.2429 | 232.0071 | 3.0918 | 232.0071 | 2.7284 | 232.0071 | 2.6701 | 232.0071 | 2.865 | 108.4514 | 4.3285 | 108.4514 | 5.792 | 108.4514 | 0.40122 | 2.9808 | 75.9303 |  | 0.036325 | 8.6653 | 53.327 | 70.607 | 6.1998 | 345.1382 | 70.607 | 7.0284 | 578.9346
1.4433 | 112.2408 |  | 7.213 | 112.2408 |  | 7.7812 | 187.1552 | 6.3669 | 330.95 | 2.5231 | 224.3716 | 2.5911 | 240.007 | 7.2675 | 240.007 | 3.218 | 240.007 | 2.8124 | 240.007 | 2.7473 | 240.007 | 2.8855 | 112.1908 | 4.3282 | 112.1908 | 5.7709 | 112.1908 | 0.37653 | 2.9894 | 74.4103 |  | 0.028774 | 8.7727 | 53.2271 | 66.1944 | 6.2252 | 340.9941 | 66.1944 | 7.0571 | 577.3044
1.4842 | 115.9802 |  | 7.1721 | 115.9802 |  | 7.8184 | 195.9101 | 6.3975 | 337.6507 | 2.5905 | 231.8503 | 2.6585 | 248.0069 | 7.2916 | 248.0069 | 3.3478 | 248.0069 | 2.8968 | 248.0069 | 2.8244 | 248.0069 | 2.9059 | 115.9302 | 4.3282 | 115.9302 | 5.7504 | 115.9302 | 0.35184 | 2.9987 | 72.8039 |  | 0.021223 | 8.9131 | 53.1272 | 61.7819 | 6.2526 | 336.7408 | 61.7819 | 7.0879 | 575.6627
1.5248 | 119.7195 |  | 7.1321 | 119.7195 |  | 7.8549 | 204.665 | 6.4271 | 344.3514 | 2.6576 | 239.329 | 2.7253 | 256.0068 | 7.3154 | 256.0068 | 3.4814 | 256.0068 | 2.9816 | 256.0068 | 2.9014 | 256.0068 | 2.9263 | 119.6695 | 4.3284 | 119.6695 | 5.7305 | 119.6695 | 0.32714 | 3.0087 | 71.0993 |  | 0.013672 | 9.1159 | 53.0273 | 57.3693 | 6.2823 | 332.3721 | 57.3693 | 7.121 | 574.0092
1.565 | 123.4589 |  | 7.0929 | 123.4589 |  | 7.8908 | 213.42 | 6.456 | 351.0522 | 2.7244 | 246.8078 | 2.7916 | 264.0067 | 7.3389 | 264.0067 | 3.619 | 264.0067 | 3.067 | 264.0067 | 2.9785 | 264.0067 | 2.9467 | 123.4089 | 4.329 | 123.4089 | 5.7112 | 123.4089 | 0.30245 | 3.0196 | 69.2824 |  | 0.0061211 | 9.4867 | 52.9274 | 52.9568 | 6.3146 | 327.8816 | 52.9568 | 7.1568 | 572.344
1.6049 | 127.1982 |  | 7.0546 | 127.1982 |  | 7.9261 | 222.1749 | 6.4842 | 357.7529 | 2.7911 | 254.2865 | 2.8574 | 272.0066 | 7.362 | 272.0066 | 3.7608 | 272.0066 | 3.153 | 272.0066 | 3.0555 | 272.0066 | 2.9671 | 127.1482 | 4.3297 | 127.1482 | 5.6924 | 127.1482 | 0.27775 | 3.0315 | 67.3352 |  |  |  |  | 48.5442 | 6.3501 | 323.262 | 48.5442 | 7.1959 | 570.6668
1.6445 | 130.9376 |  | 7.0171 | 130.9376 |  | 7.9608 | 230.9298 | 6.5116 | 364.4536 | 2.8577 | 261.7652 | 2.9228 | 280.0065 | 7.3848 | 280.0065 | 3.9071 | 280.0065 | 3.2397 | 280.0065 | 3.1327 | 280.0065 | 2.9874 | 130.8876 | 4.3308 | 130.8876 | 5.6742 | 130.8876 | 0.25306 | 3.0447 | 65.2355 |  |  |  |  | 44.1317 | 6.3892 | 318.5059 | 44.1317 | 7.2388 | 568.9776
1.6838 | 134.677 |  | 6.9803 | 134.677 |  | 7.995 | 239.6847 | 6.5385 | 371.1543 | 2.9243 | 269.2439 | 2.9879 | 288.0064 | 7.4074 | 288.0064 | 4.0583 | 288.0064 | 3.3273 | 288.0064 | 3.2101 | 288.0064 | 3.0077 | 134.627 | 4.3321 | 134.627 | 5.6564 | 134.627 | 0.22837 | 3.0594 | 62.9541 |  |  |  |  | 39.7191 | 6.4329 | 313.5972 | 39.7191 | 7.2863 | 567.2705
1.7229 | 138.4163 |  | 6.9443 | 138.4163 |  | 8.0286 | 248.4397 | 6.5648 | 377.855 | 2.991 | 276.7226 | 3.0526 | 296.0063 | 7.4296 | 296.0063 | 4.2146 | 296.0063 | 3.4159 | 296.0063 | 3.2879 | 296.0063 | 3.0279 | 138.3663 | 4.3336 | 138.3663 | 5.6392 | 138.3663 | 0.20367 | 3.0759 | 60.4525 |  |  |  |  | 35.3066 | 6.4821 | 308.5346 | 35.3066 | 7.3395 | 565.5527
1.7616 | 142.1557 |  | 6.909 | 142.1557 |  | 8.0618 | 257.1946 | 6.5905 | 384.5557 | 3.0581 | 284.2014 | 3.1171 | 304.0062 | 7.4515 | 304.0062 | 4.3765 | 304.0062 | 3.5057 | 304.0062 | 3.366 | 304.0062 | 3.0482 | 142.1057 | 4.3353 | 142.1057 | 5.6224 | 142.1057 | 0.17898 | 3.0949 | 57.6779 |  |  |  |  | 30.894 | 6.5386 | 303.3042 | 30.894 | 7.4 | 563.8205
1.8 | 145.895 |  | 6.8743 | 145.895 |  | 8.0944 | 265.9495 | 6.6158 | 391.2564 | 3.1256 | 291.6801 | 3.1815 | 312.0061 | 7.4732 | 312.0061 | 4.5445 | 312.0061 | 3.5967 | 312.0061 | 3.4447 | 312.0061 | 3.0683 | 145.845 | 4.3372 | 145.845 | 5.606 | 145.845 | 0.15428 | 3.1169 | 54.5551 |  |  |  |  | 26.4815 | 6.6043 | 297.8977 | 26.4815 | 7.47 | 562.0741
1.8382 | 149.6344 |  | 6.8403 | 149.6344 |  | 8.1266 | 274.7044 | 6.6406 | 397.9572 | 3.1937 | 299.1588 | 3.2457 | 320.006 | 7.4946 | 320.006 | 4.7193 | 320.006 | 3.6892 | 320.006 | 3.524 | 320.006 | 3.0885 | 149.5844 | 4.3393 | 149.5844 | 5.59 | 149.5844 | 0.12959 | 3.1432 | 50.9714 |  |  |  |  | 22.0689 | 6.683 | 292.3038 | 22.0689 | 7.5529 | 560.3134
1.8762 | 153.3738 |  | 6.8069 | 153.3738 |  | 8.1583 | 283.4594 | 6.665 | 404.6579 | 3.2627 | 306.6375 | 3.3098 | 328.0059 | 7.5158 | 328.0059 | 4.9017 | 328.0059 | 3.7835 | 328.0059 | 3.6042 | 328.0059 | 3.1086 | 153.3238 | 4.3415 | 153.3238 | 5.5744 | 153.3238 | 0.1049 | 3.1756 | 46.7458 |  |  |  |  | 17.6563 | 6.7803 | 286.5114 | 17.6563 | 7.6547 | 558.5385
1.9139 | 157.1131 |  | 6.7741 | 157.1131 |  | 8.1896 | 292.2143 | 6.689 | 411.3586 | 3.333 | 314.1162 | 3.374 | 336.0058 | 7.5368 | 336.0058 | 5.093 | 336.0058 | 3.8799 | 336.0058 | 3.6853 | 336.0058 | 3.1286 | 157.0631 | 4.3439 | 157.0631 | 5.5592 | 157.0631 | 0.080203 | 3.2177 | 41.5581 |  |  |  |  | 13.2438 | 6.9072 | 280.5125 | 13.2438 | 7.7863 | 556.7492
1.9513 | 160.8525 |  | 6.7418 | 160.8525 |  | 8.2205 | 300.9692 | 6.7127 | 418.0593 | 3.4048 | 321.595 | 3.4381 | 344.0057 | 7.5575 | 344.0057 | 5.2915 | 344.0057 | 3.9789 | 344.0057 | 3.7679 | 344.0057 | 3.1487 | 160.8025 | 4.3465 | 160.8025 | 5.5444 | 160.8025 | 0.055509 | 3.2767 | 34.7488 |  |  |  |  | 8.8312 | 7.0883 | 274.3037 | 8.8312 | 7.9721 | 554.9457
1.9885 | 164.5918 |  | 6.71 | 164.5918 |  | 8.251 | 309.7241 | 6.7359 | 424.76 | 3.4789 | 329.0737 | 3.5024 | 352.0056 | 7.578 | 352.0056 | 5.3362 | 352.0056 | 4.0814 | 352.0056 | 3.8525 | 352.0056 | 3.1686 | 164.5418 | 4.3492 | 164.5418 | 5.5298 | 164.5418 | 0.030815 | 3.3744 | 24.5272 |  |  |  |  | 4.4187 | 7.4018 | 267.888 | 4.4187 | 8.2905 | 553.1278
2.0255 | 168.3312 |  | 6.6788 | 168.3312 |  | 8.2811 | 318.4791 | 6.7589 | 431.4607 | 3.556 | 336.5524 | 3.5669 | 360.0055 | 7.5983 | 360.0055 | 5.3777 | 360.0055 | 4.1889 | 360.0055 | 3.9402 | 360.0055 | 3.1885 | 168.2812 | 4.3521 | 168.2812 | 5.5156 | 168.2812 | 0.0061211 | 3.6607 | 0.0201 |  |  |  |  | 0.0061211 | 10.4332 | 261.2774 | 0.0061211 | 11.3271 | 551.2957
2.0623 | 172.0706 |  | 6.6479 | 172.0706 |  | 8.3109 | 327.234 | 6.7815 | 438.1614 | 3.6373 | 344.0311 | 3.6318 | 368.0054 | 7.6184 | 368.0054 | 5.4168 | 368.0054 | 4.3049 | 368.0054 | 4.0097 | 368.0054 | 3.2084 | 172.0206 | 4.3551 | 172.0206 | 5.5017 | 172.0206
2.0988 | 175.8099 |  | 6.6176 | 175.8099 |  | 8.3402 | 335.9889 | 6.8038 | 444.8622 | 3.7252 | 351.5098 | 3.6971 | 376.0053 | 7.6383 | 376.0053 | 5.4541 | 376.0053 | 4.4262 | 376.0053 | 4.0501 | 376.0053 | 3.2282 | 175.7599 | 4.3582 | 175.7599 | 5.4881 | 175.7599
2.1352 | 179.5493 |  | 6.5877 | 179.5493 |  | 8.3693 | 344.7438 | 6.8259 | 451.5629 | 3.8246 | 358.9886 | 3.763 | 384.0052 | 7.658 | 384.0052 | 5.4897 | 384.0052 | 4.4775 | 384.0052 | 4.0888 | 384.0052 | 3.248 | 179.4993 | 4.3614 | 179.4993 | 5.4747 | 179.4993
2.1713 | 183.2886 |  | 6.5581 | 183.2886 |  | 8.3979 | 353.4988 | 6.8476 | 458.2636 | 3.9486 | 366.4673 | 3.8295 | 392.0051 | 7.6775 | 392.0051 | 5.5237 | 392.0051 | 4.5239 | 392.0051 | 4.126 | 392.0051 | 3.2678 | 183.2386 | 4.3647 | 183.2386 | 5.4616 | 183.2386
2.2073 | 187.028 |  | 6.5289 | 187.028 |  | 8.4263 | 362.2537 | 6.8691 | 464.9643 | 4.412 | 373.946 | 3.8969 | 400.005 | 7.6968 | 400.005 | 5.5564 | 400.005 | 4.5668 | 400.005 | 4.1621 | 400.005 | 3.2875 | 186.978 | 4.3681 | 186.978 | 5.4487 | 186.978
2.2431 | 190.7674 |  | 6.5001 | 190.7674 |  | 8.4544 | 371.0086 | 6.8904 | 471.665 | 5.1122 | 382.4671 | 3.9651 | 408.0049 | 7.716 | 408.0049 | 5.5878 | 408.0049 | 4.6071 | 408.0049 | 4.1973 | 408.0049 | 3.3071 | 190.7174 | 4.3716 | 190.7174 | 5.436 | 190.7174
2.2787 | 194.5067 |  | 6.4716 | 194.5067 |  | 8.4821 | 379.7636 | 6.9114 | 478.3657 | 5.2766 | 390.9882 | 4.0344 | 416.0048 | 7.735 | 416.0048 | 5.6182 | 416.0048 | 4.6453 | 416.0048 | 4.2316 | 416.0048 | 3.3267 | 194.4567 | 4.3751 | 194.4567 | 5.4236 | 194.4567
2.3142 | 198.2461 |  | 6.4434 | 198.2461 |  | 8.5095 | 388.5185 | 6.9322 | 485.0664 | 5.3941 | 399.5092 | 4.1049 | 424.0047 | 7.7538 | 424.0047 | 5.6476 | 424.0047 | 4.682 | 424.0047 | 4.2651 | 424.0047 | 3.3463 | 198.1961 | 4.3788 | 198.1961 | 5.4113 | 198.1961
2.3495 | 201.9854 |  | 6.4155 | 201.9854 |  | 8.5367 | 397.2734 | 6.9528 | 491.7672 | 5.4884 | 408.0303 | 4.1767 | 432.0046 | 7.7725 | 432.0046 | 5.6762 | 432.0046 | 4.7173 | 432.0046 | 4.2979 | 432.0046 | 3.3658 | 201.9354 | 4.3825 | 201.9354 | 5.3992 | 201.9354
2.3847 | 205.7248 |  | 6.3879 | 205.7248 |  | 8.5635 | 406.0283 | 6.9732 | 498.4679 | 5.5684 | 416.5514 | 4.2499 | 440.0045 | 7.791 | 440.0045 | 5.7039 | 440.0045 | 4.7515 | 440.0045 | 4.33 | 440.0045 | 3.3852 | 205.6748 | 4.3862 | 205.6748 | 5.3872 | 205.6748
2.4197 | 209.4642 |  | 6.3604 | 209.4642 |  | 8.5901 | 414.7833 | 6.9933 | 505.1686 | 5.6387 | 425.0725 | 4.3245 | 448.0044 | 7.8094 | 448.0044 | 5.731 | 448.0044 | 4.7847 | 448.0044 | 4.3615 | 448.0044 | 3.4047 | 209.4142 | 4.39 | 209.4142 | 5.3754 | 209.4142
2.4547 | 213.2035 |  | 6.3332 | 213.2035 |  | 8.6165 | 423.5382 | 7.0133 | 511.8693 | 5.702 | 433.5936 | 4.4003 | 456.0043 | 7.8276 | 456.0043 | 5.7573 | 456.0043 | 4.8171 | 456.0043 | 4.3923 | 456.0043 | 3.424 | 213.1535 | 4.3939 | 213.1535 | 5.3637 | 213.1535
2.4895 | 216.9429 |  | 6.3062 | 216.9429 |  | 8.6425 | 432.2931 | 7.0331 | 518.57 | 5.7598 | 442.1146 | 4.4772 | 464.0042 | 7.8456 | 464.0042 | 5.7831 | 464.0042 | 4.8486 | 464.0042 | 4.4225 | 464.0042 | 3.4434 | 216.8929 | 4.3978 | 216.8929 | 5.3522 | 216.8929
2.5241 | 220.6822 |  | 6.2794 | 220.6822 |  | 8.6683 | 441.048 | 7.0527 | 525.2707 | 5.8133 | 450.6357 | 4.5547 | 472.0041 | 7.8635 | 472.0041 | 5.8082 | 472.0041 | 4.8793 | 472.0041 | 4.4521 | 472.0041 | 3.4627 | 220.6322 | 4.4017 | 220.6322 | 5.3407 | 220.6322
2.5587 | 224.4216 |  | 6.2527 | 224.4216 |  | 8.6939 | 449.803 | 7.0721 | 531.9714 | 5.8633 | 459.1568 | 4.6324 | 480.004 | 7.8813 | 480.004 | 5.8328 | 480.004 | 4.9093 | 480.004 | 4.4811 | 480.004 | 3.4819 | 224.3716 | 4.4056 | 224.3716 | 5.3293 | 224.3716
2.5932 | 228.161 |  | 6.2261 | 228.161 |  | 8.7192 | 458.5579 | 7.0914 | 538.6721 | 5.9102 | 467.6779 | 4.7097 | 488.0039 | 7.899 | 488.0039 | 5.8569 | 488.0039 | 4.9386 | 488.0039 | 4.5096 | 488.0039 | 3.5012 | 228.111 | 4.4096 | 228.111 | 5.318 | 228.111
2.6276 | 231.9003 |  | 6.1996 | 231.9003 |  | 8.7443 | 467.3128 | 7.1105 | 545.3729 | 5.9547 | 476.199 | 4.7859 | 496.0038 | 7.9165 | 496.0038 | 5.8805 | 496.0038 | 4.9672 | 496.0038 | 4.5376 | 496.0038 | 3.5204 | 231.8503 | 4.4136 | 231.8503 | 5.3068 | 231.8503
2.662 | 235.6397 |  | 6.1732 | 235.6397 |  | 8.7692 | 476.0677 | 7.1294 | 552.0736 | 5.9969 | 484.72 | 4.8605 | 504.0037 | 7.9339 | 504.0037 | 5.9036 | 504.0037 | 4.9952 | 504.0037 | 4.5652 | 504.0037 | 3.5395 | 235.5897 | 4.4175 | 235.5897 | 5.2956 | 235.5897
2.6963 | 239.379 |  | 6.1469 | 239.379 |  | 8.7938 | 484.8227 | 7.1481 | 558.7743 | 6.0373 | 493.2411 | 4.9329 | 512.0036 | 7.9512 | 512.0036 | 5.9263 | 512.0036 | 5.0227 | 512.0036 | 4.5923 | 512.0036 | 3.5587 | 239.329 | 4.4215 | 239.329 | 5.2844 | 239.329
2.7305 | 243.1184 |  | 6.1206 | 243.1184 |  | 8.8183 | 493.5776 | 7.1668 | 565.475 | 6.076 | 501.7622 | 5.0029 | 520.0035 | 7.9683 | 520.0035 | 5.9487 | 520.0035 | 5.0495 | 520.0035 | Values of independents are not in range | 520.0035 | 3.5778 | 243.0684 | 4.4255 | 243.0684 | 5.2732 | 243.0684
2.7647 | 246.8578 |  | 6.0943 | 246.8578 |  | 8.8425 | 502.3325 | 7.1852 | 572.1757 | 6.1132 | 510.2833 | 5.0702 | 528.0034 | 7.9853 | 528.0034 | 5.9706 | 528.0034 | 5.0759 | 528.0034 | Values of independents are not in range | 528.0034 | 3.5968 | 246.8078 | 4.4294 | 246.8078 | 5.2621 | 246.8078
2.7988 | 250.5971 |  | 6.068 | 250.5971 |  | 8.8665 | 511.0874 | 7.2036 | 578.8764 | 6.1492 | 518.8044 | 5.1346 | 536.0033 | 8.0022 | 536.0033 | 5.9921 | 536.0033 | 5.1017 | 536.0033 | Values of independents are not in range | 536.0033 | 3.6159 | 250.5471 | 4.4334 | 250.5471 | 5.2509 | 250.5471
2.833 | 254.3365 |  | 6.0417 | 254.3365 |  | 8.8903 | 519.8424 | 7.2217 | 585.5771 | 6.184 | 527.3254 | 5.1962 | 544.0032 | 8.019 | 544.0032 | 6.0134 | 544.0032 | 5.1271 | 544.0032 | Values of independents are not in range | 544.0032 | 3.6349 | 254.2865 | 4.4373 | 254.2865 | 5.2397 | 254.2865
2.8671 | 258.0758 |  | 6.0153 | 258.0758 |  | 8.9139 | 528.5973 | 7.2398 | 592.2779 | 6.2177 | 535.8465 | 5.2549 | 552.0031 | 8.0357 | 552.0031 | 6.0343 | 552.0031 | 5.152 | 552.0031 | Values of independents are not in range | 552.0031 | 3.6539 | 258.0258 | 4.4412 | 258.0258 | 5.2284 | 258.0258
2.9013 | 261.8152 |  | 5.9888 | 261.8152 |  | 8.9374 | 537.3522 | 7.2577 | 598.9786 | 6.2504 | 544.3676 | 5.3109 | 560.003 | 8.0523 | 560.003 | 6.0549 | 560.003 | 5.1765 | 560.003 | Values of independents are not in range | 560.003 | 3.6729 | 261.7652 | 4.445 | 261.7652 | 5.2171 | 261.7652
2.9355 | 265.5546 |  | 5.9622 | 265.5546 |  | 8.9606 | 546.1071 | 7.2755 | 605.6793 | 6.2823 | 552.8887 | 5.3644 | 568.0029 | 8.0687 | 568.0029 | 6.0752 | 568.0029 | 5.2006 | 568.0029 | Values of independents are not in range | 568.0029 | 3.6919 | 265.5046 | 4.4488 | 265.5046 | 5.2057 | 265.5046
2.9697 | 269.2939 |  | 5.9355 | 269.2939 |  | 8.9837 | 554.8621 | 7.2932 | 612.38 | 6.3134 | 561.4098 | 5.4155 | 576.0028 | 8.0851 | 576.0028 | 6.0952 | 576.0028 | 5.2244 | 576.0028 | Values of independents are not in range | 576.0028 | 3.7109 | 269.2439 | 4.4525 | 269.2439 | 5.1942 | 269.2439
3.004 | 273.0333 |  | 5.9086 | 273.0333 |  | 9.0065 | 563.617 | 7.3107 | 619.0807 | 6.3437 | 569.9308 | 5.4644 | 584.0027 | 8.1014 | 584.0027 | 6.115 | 584.0027 | 5.2477 | 584.0027 | Values of independents are not in range | 584.0027 | 3.7299 | 272.9833 | 4.4562 | 272.9833 | 5.1826 | 272.9833
3.0383 | 276.7726 |  | 5.8814 | 276.7726 |  | 9.0292 | 572.3719 | 7.3281 | 625.7814 | 6.3734 | 578.4519 | 5.5112 | 592.0026 | 8.1175 | 592.0026 | 6.1345 | 592.0026 | 5.2708 | 592.0026 | Values of independents are not in range | 592.0026 | 3.7489 | 276.7226 | 4.4598 | 276.7226 | 5.1708 | 276.7226
3.0728 | 280.512 |  | 5.8541 | 280.512 |  | 9.0518 | 581.1268 | 7.3454 | 632.4821 | 6.4024 | 586.973 | 5.5561 | 600.0025 | 8.1336 | 600.0025 | 6.1538 | 600.0025 | 5.2935 | 600.0025 | Values of independents are not in range | 600.0025 | 3.7679 | 280.462 | 4.4634 | 280.462 | 5.1589 | 280.462
3.1074 | 284.2514 |  | 5.8264 | 284.2514 |  | 9.0741 | 589.8818 | 7.3626 | 639.1829 | 6.4308 | 595.4941 | 5.5992 | 608.0024 | 8.1495 | 608.0024 | 6.1729 | 608.0024 | 5.316 | 608.0024 | Values of independents are not in range | 608.0024 | 3.7869 | 284.2014 | 4.4668 | 284.2014 | 5.1468 | 284.2014
3.1421 | 287.9907 |  | 5.7984 | 287.9907 |  | 9.0963 | 598.6367 | 7.3797 | 645.8836 | 6.4587 | 604.0152 | 5.6407 | 616.0023 | 8.1654 | 616.0023 | 6.1917 | 616.0023 | 5.3382 | 616.0023 | Values of independents are not in range | 616.0023 | 3.8059 | 287.9407 | 4.4702 | 287.9407 | 5.1345 | 287.9407
3.1769 | 291.7301 |  | 5.7701 | 291.7301 |  | 9.1184 | 607.3916 | 7.3966 | 652.5843 | 6.4861 | 612.5362 | 5.6806 | 624.0022 | 8.1812 | 624.0022 | 6.2104 | 624.0022 | 5.3601 | 624.0022 | Values of independents are not in range | 624.0022 | 3.825 | 291.6801 | 4.4735 | 291.6801 | 5.1219 | 291.6801
3.212 | 295.4694 |  | 5.7413 | 295.4694 |  | 9.1402 | 616.1466 | 7.4135 | 659.285 | 6.513 | 621.0573 | 5.7193 | 632.0021 | 8.1969 | 632.0021 | 6.2288 | 632.0021 | 5.3817 | 632.0021 | Values of independents are not in range | 632.0021 | 3.844 | 295.4194 | 4.4766 | 295.4194 | 5.1091 | 295.4194
3.2472 | 299.2088 |  | 5.712 | 299.2088 |  | 9.162 | 624.9015 | 7.4303 | 665.9857 | 6.5394 | 629.5784 | 5.7566 | 640.002 | 8.2124 | 640.002 | 6.2471 | 640.002 | 5.403 | 640.002 | Values of independents are not in range | 640.002 | 3.8632 | 299.1588 | 4.4796 | 299.1588 | 5.096 | 299.1588
3.2828 | 302.9482 |  | 5.6822 | 302.9482 |  | 9.1835 | 633.6564 | 7.4469 | 672.6864 | 6.5655 | 638.0995 | 5.7928 | 648.0019 | 8.2279 | 648.0019 | 6.2651 | 648.0019 | 5.424 | 648.0019 | Values of independents are not in range | 648.0019 | 3.8824 | 302.8982 | 4.4825 | 302.8982 | 5.0825 | 302.8982
3.3186 | 306.6875 |  | 5.6518 | 306.6875 |  | 9.2049 | 642.4113 | 7.4634 | 679.3871 | 6.5911 | 646.6206 | 5.8279 | 656.0018 | 8.2434 | 656.0018 | 6.283 | 656.0018 | Values of independents are not in range | 656.0018 | Values of independents are not in range | 656.0018 | 3.9016 | 306.6375 | 4.4852 | 306.6375 | 5.0687 | 306.6375
3.3547 | 310.4269 |  | 5.6207 | 310.4269 |  | 9.2262 | 651.1663 | 7.4799 | 686.0879 | 6.6163 | 655.1416 | 5.862 | 664.0017 | 8.2587 | 664.0017 | 6.3007 | 664.0017 | Values of independents are not in range | 664.0017 | Values of independents are not in range | 664.0017 | 3.921 | 310.3769 | 4.4877 | 310.3769 | 5.0544 | 310.3769
3.3912 | 314.1662 |  | 5.5888 | 314.1662 |  | 9.2474 | 659.9212 | 7.4962 | 692.7886 | 6.6411 | 663.6627 | 5.8951 | 672.0016 | 8.2739 | 672.0016 | 6.3183 | 672.0016 | Values of independents are not in range | 672.0016 | Values of independents are not in range | 672.0016 | 3.9404 | 314.1162 | 4.49 | 314.1162 | 5.0396 | 314.1162
3.4282 | 317.9056 |  | 5.5561 | 317.9056 |  | 9.2684 | 668.6761 | 7.5125 | 699.4893 | 6.6657 | 672.1838 | 5.9274 | 680.0015 | 8.2891 | 680.0015 | 6.3356 | 680.0015 | Values of independents are not in range | 680.0015 | Values of independents are not in range | 680.0015 | 3.9599 | 317.8556 | 4.4921 | 317.8556 | 5.0243 | 317.8556
3.4657 | 321.645 |  | 5.5223 | 321.645 |  | 9.2892 | 677.431 | 7.5287 | 706.19 | 6.6898 | 680.7049 | 5.9589 | 688.0014 | 8.3042 | 688.0014 | 6.3529 | 688.0014 | Values of independents are not in range | 688.0014 | Values of independents are not in range | 688.0014 | 3.9796 | 321.595 | 4.494 | 321.595 | 5.0084 | 321.595
3.5037 | 325.3843 |  | 5.4874 | 325.3843 |  | 9.3099 | 686.186 | 7.5447 | 712.8907 | 6.7137 | 689.226 | 5.9896 | 696.0013 | 8.3192 | 696.0013 | 6.37 | 696.0013 | Values of independents are not in range | 696.0013 | Values of independents are not in range | 696.0013 | 3.9994 | 325.3343 | 4.4955 | 325.3343 | 4.9917 | 325.3343
3.5424 | 329.1237 |  | 5.4512 | 329.1237 |  | 9.3305 | 694.9409 | 7.5607 | 719.5914 | 6.7373 | 697.747 | 6.0196 | 704.0012 | 8.3341 | 704.0012 | 6.3869 | 704.0012 | Values of independents are not in range | 704.0012 | Values of independents are not in range | 704.0012 | 4.0193 | 329.0737 | 4.4968 | 329.0737 | 4.9742 | 329.0737
3.5819 | 332.863 |  | 5.4134 | 332.863 |  | 9.351 | 703.6958 | 7.5766 | 726.2921 | 6.7606 | 706.2681 | 6.049 | 712.0011 | 8.349 | 712.0011 | 6.4037 | 712.0011 | Values of independents are not in range | 712.0011 | Values of independents are not in range | 712.0011 | 4.0395 | 332.813 | 4.4976 | 332.813 | 4.9558 | 332.813
3.6223 | 336.6024 |  | 5.3738 | 336.6024 |  | 9.3713 | 712.4507 | 7.5924 | 732.9929 | 6.7836 | 714.7892 | 6.0776 | 720.001 | 8.3638 | 720.001 | 6.4203 | 720.001 | Values of independents are not in range | 720.001 | Values of independents are not in range | 720.001 | 4.0599 | 336.5524 | 4.498 | 336.5524 | 4.9362 | 336.5524
3.6638 | 340.3418 |  | 5.332 | 340.3418 |  | 9.3915 | 721.2057 | 7.6081 | 739.6936 | 6.8063 | 723.3103 | 6.1057 | 728.0009 | 8.3785 | 728.0009 | 6.4368 | 728.0009 | Values of independents are not in range | 728.0009 | Values of independents are not in range | 728.0009 | 4.0806 | 340.2918 | 4.4979 | 340.2918 | 4.9152 | 340.2918
3.7067 | 344.0811 |  | 5.2876 | 344.0811 |  | 9.4116 | 729.9606 | 7.6237 | 746.3943 | 6.8288 | 731.8314 | 6.1333 | 736.0008 | 8.3931 | 736.0008 | 6.4532 | 736.0008 | Values of independents are not in range | 736.0008 | Values of independents are not in range | 736.0008 | 4.1017 | 344.0311 | 4.4972 | 344.0311 | 4.8927 | 344.0311
3.7513 | 347.8205 |  | 5.2402 | 347.8205 |  | 9.4316 | 738.7155 | 7.6393 | 753.095 | 6.851 | 740.3524 | 6.1603 | 744.0007 | 8.4076 | 744.0007 | 6.4694 | 744.0007 | Values of independents are not in range | 744.0007 | Values of independents are not in range | 744.0007 | 4.1232 | 347.7705 | 4.4958 | 347.7705 | 4.8683 | 347.7705
3.7982 | 351.5598 |  | 5.1891 | 351.5598 |  | 9.4514 | 747.4704 | 7.6547 | 759.7957 | 6.8731 | 748.8735 | 6.1868 | 752.0006 | 8.4221 | 752.0006 | 6.4855 | 752.0006 | Values of independents are not in range | 752.0006 | Values of independents are not in range | 752.0006 | 4.1456 | 351.5098 | 4.4937 | 351.5098 | 4.8417 | 351.5098
3.8479 | 355.2992 |  | 5.133 | 355.2992 |  | 9.4712 | 756.2254 | 7.6701 | 766.4964 | 6.8948 | 757.3946 | 6.2128 | 760.0005 | 8.4365 | 760.0005 | 6.5015 | 760.0005 | Values of independents are not in range | 760.0005 | Values of independents are not in range | 760.0005 | 4.1689 | 355.2492 | 4.4905 | 355.2492 | 4.8121 | 355.2492
3.9017 | 359.0386 |  | 5.0702 | 359.0386 |  | 9.4908 | 764.9803 | 7.6854 | 773.1971 | 6.9164 | 765.9157 | 6.2384 | 768.0004 | 8.4509 | 768.0004 | 6.5174 | 768.0004 | Values of independents are not in range | 768.0004 | Values of independents are not in range | 768.0004 | 4.1935 | 358.9886 | 4.486 | 358.9886 | 4.7786 | 358.9886
3.9614 | 362.7779 |  | 4.9979 | 362.7779 |  | 9.5103 | 773.7352 | 7.7007 | 779.8979 | 6.9378 | 774.4368 | 6.2636 | 776.0003 | 8.4652 | 776.0003 | 6.5332 | 776.0003 | Values of independents are not in range | 776.0003 | Values of independents are not in range | 776.0003 | 4.2201 | 362.7279 | 4.4797 | 362.7279 | 4.7394 | 362.7279
4.0309 | 366.5173 |  | 4.91 | 366.5173 |  | 9.5297 | 782.4901 | 7.7158 | 786.5986 | 6.9589 | 782.9578 | 6.2884 | 784.0002 | 8.4794 | 784.0002 | 6.5488 | 784.0002 | Values of independents are not in range | 784.0002 | Values of independents are not in range | 784.0002 | 4.2502 | 366.4673 | 4.4706 | 366.4673 | 4.6909 | 366.4673
4.1217 | 370.2566 |  | 4.7894 | 370.2566 |  | 9.5489 | 791.2451 | 7.7309 | 793.2993 | 6.9799 | 791.4789 | 6.3128 | 792.0001 | 8.4935 | 792.0001 | 6.5644 | 792.0001 | Values of independents are not in range | 792.0001 | Values of independents are not in range | 792.0001 | 4.288 | 370.2066 | 4.4558 | 370.2066 | 4.6236 | 370.2066
4.3883 | 373.936 |  | 4.4126 | 373.936 |  | 9.5681 | 800 | 7.7459 | 800 | 7.0006 | 800 | 6.3368 | 800 | 8.5076 | 800 | 6.5798 | 800 | Values of independents are not in range | 800 | Values of independents are not in range | 800 | 4.412 | 373.946 | 4.412 | 373.946 | 4.412 | 373.946